## Summary
Label | Converged | Maximum Bus Mismatch | System Mismatch | Solution termination state | Flow Violations # | Flow Violations Largest % | Low Range Violations # | Low Range Violations Largest | High Range Violations # | High Range Violations Largest | Deviation Violations # | Deviation Violations Largest | # Disconnect Island Buses | Seq #
BASE CASE | 1 | 0.04 | 0.14 | MET CONVERGENCE TOLERANCE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
SING OPN LIN 1 1-4(T1) | 1 | 0 | 0 | MET CONVERGENCE TOLERANCE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 2
SING OPN LIN 2 2-7(T2) | 0 | 211.31 | 516.99 | BLOWN UP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3
SING OPN LIN 3 3-9(T3) | 1 | 0.09 | 0.24 | MET CONVERGENCE TOLERANCE | 3 | 122.66 | 4 | 0.7896 | 0 | 0 | 0 | 0 | 1 | 4
SING OPN LIN 4 4-5(1) | 0 | 343.53 | 1078.06 | BLOWN UP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
SING OPN LIN 5 4-6(1) | 0 | 127.1 | 210.61 | ITERATION LIMIT EXCEEDED | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6
SING OPN LIN 6 5-7(1) | 0 | 696.39 | 2118.64 | BLOWN UP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7
SING OPN LIN 7 6-9(1) | 1 | 0 | 0.01 | MET CONVERGENCE TOLERANCE | 3 | 183.15 | 3 | 0.7024 | 0 | 0 | 0 | 0 | 0 | 8
SING OPN LIN 8 7-8(1) | 1 | 0.06 | 0.13 | MET CONVERGENCE TOLERANCE | 2 | 236.5 | 3 | 0.7424 | 0 | 0 | 0 | 0 | 0 | 9
SING OPN LIN 9 8-9(1) | 1 | 0.09 | 0.34 | MET CONVERGENCE TOLERANCE | 3 | 175.3 | 3 | 0.8445 | 0 | 0 | 0 | 0 | 0 | 10

## Flow violations
Monitored Element | Network Label | Others | Base Flow | Maximum Flow | Impact | Rate | % | Branch Angle Difference (Rad) | Available Capacity | Seq #
4 BUS4 230.00 5 BUS5 230.00 1 | SING OPN LIN 9 8-9(1) | 0 | 167.06 | 270.93 | 315.43 | 250 | 126.17 | -0.2729 | -65.43 | 1
4 BUS4 230.00 6 BUS6 230.00 1 | SING OPN LIN 7 6-9(1) | 0 | 93.14 | 223.26 | 317.84 | 250 | 127.14 | -0.303 | -67.84 | 2
5 BUS5 230.00 7 BUS7 230.00 1 | SING OPN LIN 7 6-9(1) | 0 | 154.09 | 255.21 | 351.95 | 250 | 140.78 | 0.6528 | -101.95 | 3
6 BUS6 230.00 9 BUS9 230.00 1 | SING OPN LIN 9 8-9(1) | 0 | 133.21 | 233.19 | 262.95 | 150 | 175.3 | 0.4567 | -112.95 | 4
7 BUS7 230.00 8 BUS8 230.00 1 | SING OPN LIN 9 8-9(1) | 0 | 135.99 | 263.33 | 311.81 | 250 | 124.73 | -0.2165 | -61.81 | 5
8 BUS8 230.00 9 BUS9 230.00 1 | SING OPN LIN 8 7-8(1) | 0 | 127.63 | 263.35 | 354.75 | 150 | 236.5 | 0.3542 | -204.75 | 6

## Voltage violations
Network Label | Bus | Voltage | Violation | Seq #
SING OPN LIN 3 3-9(T3) | 5 BUS5 23 | 0.8146 | 0.0854 | 1
SING OPN LIN 3 3-9(T3) | 6 BUS6 23 | 0.7896 | 0.1104 | 2
SING OPN LIN 3 3-9(T3) | 8 BUS8 23 | 0.8406 | 0.0594 | 3
SING OPN LIN 3 3-9(T3) | 9 BUS9 23 | 0.8339 | 0.0661 | 4
SING OPN LIN 7 6-9(1) | 4 BUS4 23 | 0.8791 | 0.0209 | 5
SING OPN LIN 7 6-9(1) | 5 BUS5 23 | 0.7251 | 0.1749 | 6
SING OPN LIN 7 6-9(1) | 6 BUS6 23 | 0.7024 | 0.1976 | 7
SING OPN LIN 8 7-8(1) | 5 BUS5 23 | 0.831 | 0.069 | 8
SING OPN LIN 8 7-8(1) | 6 BUS6 23 | 0.8771 | 0.0229 | 9
SING OPN LIN 8 7-8(1) | 8 BUS8 23 | 0.7424 | 0.1576 | 10
SING OPN LIN 9 8-9(1) | 5 BUS5 23 | 0.8589 | 0.0411 | 11
SING OPN LIN 9 8-9(1) | 6 BUS6 23 | 0.8868 | 0.0132 | 12
SING OPN LIN 9 8-9(1) | 8 BUS8 23 | 0.8445 | 0.0555 | 13